## Project
Project intake - Single Line Diagram Assignment 6_16.docx
Fill the Value column. Yellow rows are required before drafting starts.
Field | Value | What it is
job | ASSIGNMENT-6-16 | IOM job number, e.g. 8372
customer |  | End customer name
title | Develop a Single-Line Diagram from Project Requirements | Project title as it appears in the title block
location_code | +A01 | e.g. +A01
sheet_standard | 8508 | Which drawing standard / frame profile to use
system_voltage | 13.8kV | Nominal system voltage, e.g. 4.16kV
bus_rating | 1200A | Continuous bus rating, e.g. 4000A
bus_ka_rating | 25kA | Bus short-circuit rating, e.g. 50kA
phases | 3 | e.g. 3
wires |  | e.g. 3W
frequency | 60HZ | e.g. 60HZ
available_sc_current | 25kA | Available short-circuit current AT the switchgear (Incoming Power spec)
bil |  | Basic insulation level, if shown on the bus label
grounding |  | System grounding arrangement
drawing_no |  | e.g. 8372+A01-001
rev
date
engineer
drawn
checked
approved

## Units
unit | bus | deck | tag | schema_type | status | description | voltage | amp_rating | ka_rating | relay | relay_2 | relay_functions | ct_protection | ct_metering | ct_ground | pt | pt_connection | pt_primary_fuse | pt_secondary_fuse | pt_reference | cable | destination | arrester | diff_note
1 | A | single | 52-M | utility_incoming |  | MAIN BREAKER | 15kV | 1200A | 25kA | SEL-751 |  |  | 1200:5A (3) |  |  | 14,400:120V | grounded-wye to grounded-wye |  |  |  |  | UTILITY SUPPLY 13.8kV, 3PH, 60HZ
2 | A | single | 52-F1 | feeder_breaker |  | TRANSFORMER FEEDER | 15kV | 600A | 25kA | SEL-751 |  |  | 200:5A (3) | [6 empty] | VOLTAGE REFERENCE FROM BUS PT |  | TO 2500kVA XFMR 13.8kV-480Y/277V Z=5.75%
3 | A | single | 52-F2 | motor_feeder |  | MOTOR FEEDER | 15kV | 600A | 25kA | SEL-710 |  |  | 100:5A (3) |  | 50:5A |  |  |  |  | VOLTAGE REFERENCE FROM BUS PT |  | TO 1500HP 13.8kV MOTOR
4 | A | single | 52-F3 | feeder_breaker | FUTURE | FUTURE FEEDER | 15kV | 600A | 25kA | SEL-751 |  |  | 400:5A (3) | [6 empty] | VOLTAGE REFERENCE FROM BUS PT |  | RESERVED FOR FUTURE LOAD
Note on C1: single / upper / lower, for two-high cubicles.
Note on D1: Device tag, e.g. 52-GEN1A. Unique within the lineup.
Note on E1: Which entry in this catalogue the cubicle is.
Note on F1: Blank for a normal in-service feeder, or SPARE / FUTURE. The two words mean the same thing; the drawing prints whichever is entered.
Note on H1: Breaker rated maximum voltage, e.g. 4.76KV.
Note on I1: Breaker continuous current rating.
Note on J1: Breaker interrupting rating.
Note on K1: Primary protection relay model.
Note on L1: Second relay, where the cubicle carries one. On an incomer this is the bus differential, e.g. SEL-787.
Note on M1: ANSI device numbers shown in the relay box, e.g. 25, 50P, 51P, 50G, 51G.
Note on N1: Protection CT ratio and quantity, e.g. 400:5A (3).
Note on O1: Metering CT ratio and quantity. Present only where a metering relay is specified.
Note on P1: Separate ground-fault / core-balance CT ratio. Motor feeders only.
Note on Q1: Voltage transformer set, e.g. (3) 4160/230V.
Note on R1: PT connection -- open delta (usual) or wye-wye.
Note on S1: PT primary fuse, e.g. CLF 0.5E.
Note on T1: PT secondary fuse, e.g. FU1/6A.
Note on U1: What the PT secondary feeds, e.g. LINE PT REFERENCE TO INTELIMAINS RELAY IN MCP.
Note on V1: Incoming / outgoing cable size and quantity, e.g. 750kcmil (1)/PH.
Note on W1: Source or load text printed at the cubicle entry / exit.
Note on X1: Surge arrester rating. Blank where the lineup has none.
Note on Y1: Bus-differential cross-reference note.

## Schema types
Schema-type catalogue
Green = specified by TPPES. Amber = reverse-engineered from an issued drawing, needs confirming. Plain = already built in sld_config.json.
Schema type | Title | What's in the cubicle | Required intake fields | Status / source
motor_feeder | Feeder 2 - Motor Feeder | feeder breaker + phase CTs + ground-fault CT + motor protection relay | voltage, amp_rating, ka_rating, relay, ct_protection, ct_ground, destination | specified TPPES
utility_incoming | Incoming Power | incoming cable termination + main breaker + protection CTs + (3) VTs + PT secondary protection + protection relay + differential relay (optional) | voltage, amp_rating, ka_rating, relay, ct_protection, pt, pt_connection, pt_secondary_fuse, cable, destination | specified TPPES
main_with_bus_pt | Main breaker with bus PT in the same cubicle | bus PT + PT primary fuse + main breaker + CT + relay | voltage, amp_rating, ka_rating, relay, ct_protection, pt, pt_primary_fuse, destination | proposed drawing 8372 unit 6
gen_with_line_pt | Generator feeder with line PT in the same cubicle | line PT + PT fuse + gen breaker + CT + relay | voltage, amp_rating, ka_rating, relay, ct_protection, pt, destination | proposed drawing 8372 unit 11
gen_feeder | Generator incoming feeder | drawout breaker + protection CT + metering CT + arrester + 86 lockout + relay | voltage, amp_rating, ka_rating, relay, ct_protection, destination | defined sld_config.json (8508)
customer_feeder | Feeder 1 - Customer / load feeder | drawout breaker + protection CT + metering CT + arrester + 86 lockout + relay + control transformer | voltage, amp_rating, ka_rating, relay, ct_protection, destination | defined sld_config.json (8508), confirmed by TPPES as Feeder 1
bess_feeder | BESS feeder | drawout breaker + protection CT + metering CT + arrester + 86 lockout + relay + second fuse | voltage, amp_rating, ka_rating, relay, ct_protection, destination | defined sld_config.json (8508)
xfmr_feeder | Transformer feeder | fused MV disconnect + Kirk key + CT + feeder transformer + PP-1 panel + lighting transformer + LP-1 panel | ct_metering, destination | defined sld_config.json (8508)
xfmr_riser | Transformer feeder continuation | fused MV disconnect + Kirk key + CT | ct_metering, destination | defined sld_config.json (8508)
pt_riser_tie | Bus PT / riser adjacent to a tie | bus PT + PT fuse + relay | relay | defined sld_config.json (8508)
pt_riser | Bus PT / riser referencing the other bus | bus PT + PT fuse + relay + differential lead + cross-reference note | relay, diff_note | defined sld_config.json (8508)
main_tie | Main / tie breaker | drawout breaker + three CTs + two CPT fuses + relay with sync + 86 lockout | voltage, amp_rating, ka_rating, relay, ct_protection | defined sld_config.json (8508)
Cubicle arrangements
Not schema types. A schema type says what a cubicle contains; an arrangement says how it is subdivided. Any schema type can sit in any arrangement.
Arrangement | deck values | Description | Status
single_high | single | One unit per cubicle. Every issued drawing reviewed so far uses this for generator and main cubicles. | supported
two_high | upper / lower | Two breakers stacked in one cubicle, each taking its own schema type. One row per deck, both rows carrying the same unit number. | blocked Role positions in sld_config.json are absolute sheet elevations, so a deck offset cannot be expressed. Needs the slot refactor.
Resolved with TPPES
✓ Feeder 1 is customer_feeder. Confirmed by TPPES.
✓ FUTURE and SPARE mean the same thing. 'future_feeder' has been removed as a schema type -- it is now the status field on any feeder type, and the sheet prints whichever word is entered.
✓ The utility main with an 87 differential is not its own type. 'utility_main_787' has been folded into utility_incoming, with the differential relay entered in relay_2.
✓ Motor feeders carry metering CTs only when the customer specifies a metering relay, so ct_metering is optional on that type.
✓ PT connection is usually open delta, sometimes wye-wye. Both are offered; open delta is the default.
Still open
• Motor feeder: is the ground-fault CT a core-balance (zero-sequence) CT, or residual from the phase CTs? Changes the symbol and the three-line.
• Does SEL-710 need its own relay-box block, or does the existing relay box take any model as text?
• Two-high: does the upper deck always sit on the line side and the lower on the load side, or does it vary by job?

## Field guide
What each column on the Units tab means
Column | Meaning
tag | Device tag, e.g. 52-GEN1A. Unique within the lineup.
schema_type | Which entry in this catalogue the cubicle is.
status | Blank for a normal in-service feeder, or SPARE / FUTURE. The two words mean the same thing; the drawing prints whichever is entered.
voltage | Breaker rated maximum voltage, e.g. 4.76KV.
amp_rating | Breaker continuous current rating.
ka_rating | Breaker interrupting rating.
relay | Primary protection relay model.
relay_2 | Second relay, where the cubicle carries one. On an incomer this is the bus differential, e.g. SEL-787.
relay_functions | ANSI device numbers shown in the relay box, e.g. 25, 50P, 51P, 50G, 51G.
ct_protection | Protection CT ratio and quantity, e.g. 400:5A (3).
ct_metering | Metering CT ratio and quantity. Present only where a metering relay is specified.
ct_ground | Separate ground-fault / core-balance CT ratio. Motor feeders only.
pt | Voltage transformer set, e.g. (3) 4160/230V.
pt_connection | PT connection -- open delta (usual) or wye-wye.
pt_primary_fuse | PT primary fuse, e.g. CLF 0.5E.
pt_secondary_fuse | PT secondary fuse, e.g. FU1/6A.
pt_reference | What the PT secondary feeds, e.g. LINE PT REFERENCE TO INTELIMAINS RELAY IN MCP.
cable | Incoming / outgoing cable size and quantity, e.g. 750kcmil (1)/PH.
destination | Source or load text printed at the cubicle entry / exit.
arrester | Surge arrester rating. Blank where the lineup has none.
diff_note | Bus-differential cross-reference note.
deck | single / upper / lower, for two-high cubicles.