## units
unit | bus | tag | description | archetype | voltage | amp_rating | ka_rating | relay | destination | ct_protection | ct_metering | arrester | diff_note
1 | A | 52-GEN1 |  | gen_feeder | 17.5kV | 3150A | 40kA | SEL-751-GEN1 FEEDER PROTECTION RELAY | INCOMING 13.8KV LINE FROM GEN-1 | 400:5A (3) | 3000:5A (3) | L.A. 18kV 15.3kV MCOV
2 | A | 52-F1 | CUSTOMER FEEDER | customer_feeder | 17.5kV | 3150A | 40kA | SEL-751-F1 FEEDER PROTECTION RELAY | CUSTOMER FEEDER 1 | 400:5A (3) | 3000:5A (3) | L.A. 18kV 15.3kV MCOV
3 | A | PT | BUS PT | pt_riser_tie | 17.5kV |  |  | GE-850-A FEEDER PROTECTION RELAY WITH HID MODULE
Note on A1: Cubicle number printed as "UNIT n". Position on the sheet comes from ROW ORDER, not this number.
Note on B1: A or B. build_sld.py --bus filters on this to split a lineup across sheets.
Note on C1: Device tag, e.g. 52-GEN1. Printed above the cubicle and inside the breaker box. Must be unique.
Note on D1: Second line under the tag, e.g. CUSTOMER FEEDER. Leave blank if the tag says enough.
Note on E1: Which unit template to draw. Pick from the dropdown; see the Archetypes tab.
Note on F1: First line of the breaker spec block, e.g. 17.5kV.
Note on G1: Breaker continuous rating, e.g. 3150A. NOT the same as the bus label - see the Before you build tab.
Note on H1: Breaker interrupting rating, e.g. 40kA.
Note on I1: Full relay description. Printed in the relay box; wraps automatically.
Note on J1: Where the feeder goes. Printed below the cubicle at the outgoing arrow.
Note on K1: Protection CT ratio, e.g. 400:5A (3). Fills the upper CT label.
Note on L1: Metering CT ratio, e.g. 3000:5A (3). Fills the lower CT label.
Note on M1: DEAD COLUMN - read and discarded. The rating is baked into the ARRESTER block artwork, so editing this changes nothing on the drawing.
Note on N1: Bus-differential note. Only used by the pt_riser archetype; leave blank otherwise.

## Before you build
Sample 3-unit switchgear - how to use this file
Step 1 Edit the "units" tab. One row per cubicle, top to bottom.
Step 2 File > Save As > CSV UTF-8, name it e.g. sample_3unit_units.csv
Step 3 Run the three commands below from the SLD_AUTOMATION folder.
python preflight.py sample_3unit_units.csv
python build_sld.py sample_3unit_units.csv sample_3unit.dxf --bus A
python preview.py sample_3unit.dxf sample_3unit.png
Cubicle position comes from row order, not the unit number. Units need not be contiguous or start at 1 - they only have to be in the order you want them drawn.
Five things this spreadsheet does NOT control
Check these in sld_config.json before issuing. preflight.py flags the first four.
Setting | Current value | Why it matters
sheet.bus_label | 17.5KV, 3150A / 3PH, 40KAIC, BIL 95kV / BUS {bus} | Fixed text. A 2000A lineup still gets labelled 3150A. Nothing in the CSV changes it.
sheet.pitch | 3.61 | Cubicle width. Set it to the widest unit in the new lineup, per IOM practice.
sheet.bus_y / cubicle_top / cubicle_bottom | 18.583 / 20.602 / 9.435 | Sheet elevations. Only touch these if the new drawing frame differs.
ARRESTER block text | L.A. 18kV 15.3kV MCOV | Baked into the block as MTEXT, so identical on every unit. The arrester column in the units tab is read and discarded.
Symbol library | symbol_library.dxf | A unit type needing a symbol the library lacks prints "MISSING from library" at build time.

## Archetypes
Archetype | What it draws | Devices | Columns it consumes
gen_feeder | Generator incoming feeder -- drawout breaker, dual CT, arrester | 13 | ct_metering, ct_protection
customer_feeder | Customer feeder -- gen feeder plus control transformer | 14 | ct_metering, ct_protection
bess_feeder | BESS feeder -- gen feeder plus second fuse | 14 | ct_metering, ct_protection
xfmr_feeder | Transformer feeder -- fused disconnect with Kirk key, one CT, and the load-side one-line down to the LV panels (reference unit 8) | 16 | ct_metering
xfmr_riser | Transformer feeder continuation -- same disconnect, Kirk key and CT, but terminating on a connector instead of a transformer (reference unit 14) | 8 | ct_metering
pt_riser_tie | Bus PT / riser adjacent to a tie -- its relay takes the differential CT from the tie unit (reference unit 9) | 3 | (none beyond the common ones)
pt_riser | Bus PT / riser whose differential CT comes from the other bus, on another sheet (reference unit 11) | 5 | diff_note
main_tie | Main / tie breaker -- three CTs, two CPT fuses, breaker stack lowered to clear the upper CT, outgoing run leaving sideways | 18 | ct_metering, ct_protection
Every archetype also uses: unit, bus, tag, description, voltage, amp_rating, ka_rating, relay, destination.