## Project
Project intake - supplied once per job
Fill the Value column. Yellow rows are required before drafting starts.
Field | Value | What it is
job |  | IOM job number, e.g. 8372
customer |  | End customer name
title | REHABILITACION SUBESTACION "C" 115/34.5 KV | Project title as it appears in the title block
location_code |  | e.g. +A01
sheet_standard |  | Which drawing standard / frame profile to use
system_voltage | 34.5KV | Nominal system voltage, e.g. 4.16kV
bus_rating | 2500A | Continuous bus rating, e.g. 4000A
bus_ka_rating | 31.5KA | Bus short-circuit rating, e.g. 50kA
phases | 3 | e.g. 3
wires | 3W | e.g. 3W
frequency | 60HZ | e.g. 60HZ
available_sc_current | 31.5KA | Available short-circuit current AT the switchgear (Incoming Power spec)
bil |  | Basic insulation level, if shown on the bus label
grounding |  | System grounding arrangement
drawing_no |  | e.g. 8372+A01-001
rev
date
engineer
drawn
checked
approved

## Units
unit | bus | deck | tag | description | voltage | amp_rating | ka_rating | relay | relay_fuse | bus_differential | ct_protection | ct_differential | ct_metering | ct_ground | ct_class | pt | pt_primary_fuse | destination
1 | 1 | single | B-180 | INCOMER BUS 1 | 40.5KV | 2500A | 31.5KA | 7SJ85 P1J2253039 R-4 |  |  | 2500:5/5A (3) | 2500:5/5A (3) |  |  | 5P20/5P20 |  |  | TX "B" 40/66MVA 115/34.5KV
2 | 1 | single | PT BUS 1 | POTENTIAL TRANSFORMER BUS 1 | [11 empty] | 34.5KV:120V | 0.5A
3 | 1 | single | TX AUX 1 | TX AUX 1 | 40.5KV | 630A | 31.5KA | 7SJ85 P1J1617696 R-10 |  |  | 600:5/5A (3) | 600:5/5A (3) |  |  | 5P20/5P20 |  |  | TX AUX 1
4 | 1 | single | B-105 | CTO. 13C | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-3 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. 13C
5 | 1 | single | B-205 | CTO. C | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-2 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. C
6 | 1 | single | B-305 | CTO. 15B | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-1 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. 15B
7 | 1 | single | B130 | BUS TIE | 40.5KV | 2500A | 31.5KA | 7SJ85 P1J1120691 R-9 |  | 87B | 2500:5/5A (3) | 2500:5/5A (3) |  |  | 5P20/5P20 |  |  | BUS 2
8 | 2 | single |  | RISER
9 | 2 | single | B-405 | CTO. 15A | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-7 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. 15A
10 | 2 | single | B-505 | CTO. 19C | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-6 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. 19C
11 | 2 | single | B-605 | CTO. 14C | 40.5KV | 1250A | 31.5KA | 7SJ85 P1J2253039 R-5 |  |  | 1200:5/5A (3) | 1200:5/5A (3) |  |  | 5P20/5P20 |  |  | CTO. 14C
12 | 2 | single | TX AUX 2 | TX AUX 2 | 40.5KV | 630A | 31.5KA | 7SJ85 P1J1617696 R-11 |  |  | 600:5/5A (3) | 600:5/5A (3) |  |  | 5P20/5P20 |  |  | TX AUX 2
13 | 2 | single | PT BUS 2 | POTENTIAL TRANSFORMER BUS 2 | [11 empty] | 34.5KV:120V | 0.5A
14 | 2 | single | B-280 | INCOMER BUS 2 | 40.5KV | 2500A | 31.5KA | 7SJ85 P1J2253039 R-8 |  |  | 2500:5/5A (3) | 2500:5/5A (3) |  |  | 5P20/5P20 |  |  | TX "A" 40/66MVA 115/34.5KV
15 | 2 | single |  | SPARE
16 | 2 | single |  | SPARE

## Field guide
What each column on the Units tab means
Column | Meaning
unit | Cubicle number. Two rows share it on a two-high cubicle.
bus | Which bus the cubicle sits on.
deck | single, or upper / lower for the two decks of a two-high cubicle.
tag | Device tag, e.g. 52-GEN1A. Unique within the lineup.
description | Cubicle title printed under the unit number.
voltage | Breaker rated maximum voltage, e.g. 15kV.
amp_rating | Breaker continuous current. BLANK MEANS NO BREAKER -- that is how a deck holds only a bus PT.
ka_rating | Breaker interrupting rating.
relay | Protection relay model. Drawn as a labelled box beside the breaker.
relay_fuse | Optional. Fuse on this relay's supply where it drops off the reference run, e.g. 6A. Leave blank to take the house default.
bus_differential | Fill on the ONE cubicle whose relay is the bus differential relay, e.g. 87B. Every ct_differential in the lineup is wired to it. Leave blank everywhere else -- and if no cubicle states it, the differential CTs are drawn with no run, because there is nothing for them to run to.
ct_protection | Protection CT ratio and quantity, e.g. 400:5A (3).
ct_differential | Ratio of the CT feeding bus differential, e.g. 1200:5A (3). A dual-core CT (1200/5/5A) is one device in the panel schedule and two symbols here, because the two cores feed different circuits. On a tie this is the far bus's differential.
ct_metering | Metering CT. Fill this ONLY if the cubicle really has a second CT set -- leaving it blank is what keeps one-CT feeders to one CT.
ct_ground | Separate ground-fault CT, e.g. 50:5A. Motor feeders.
ct_class | Optional. Accuracy class stamped on every CT in this cubicle, e.g. 5P20. Leave blank to take the house default for each CT's job (5P20 protection, 0.3B1.8 metering, GND CT).
pt | Bus PT ratio, e.g. 14,400:120V. The cubicle that states this gets the PT branch, and its secondary feeds every relay in the lineup.
pt_primary_fuse | PT primary fuse, e.g. CLF 0.5E. The secondary fuse belongs on the three-line diagram, not here.
destination | Source or load text printed at the cubicle entry / exit. A future feeder is a normal feeder whose destination says so.
A device is drawn if and only if its cell has a value.