## BOM
Item No. | Manufacturer | Part Number | Description | Quantity | Application
1 | GEIS | VB2PLUS- 17.5/T3150-40kA | 17.5kV, 3150A, 40kA | 15 | CB
2 | GEIS | JDZXR22-15C | Potential transformer, 7.98kV/120V, 1 per phase | 12 | BUS PTs
3 | GEIS | LZZB-17.5 185/D2 | 400-3000/5/5A 5P20/5P20 3.75/3.75VA 40kA/1s | 30 | GEN CTs for 751
4 | GEIS | LZZB-17.5 185/D2 | 800-3000/5/5A 5P20/5P20 7.5/7.5VA 40kA/1s | 6 | FDR CTs (unit 7 &13)
5 | GEIS | LZZB-17.5 185/D2 | 3000/5/5A 5P20/5P20 30/30VA 40kA/1s | 9 | TIE CTs
6 | GEIS | LZZB-17.5 185/D2 | 3000/5A 5P20 30VA 40kA/1s | 9 | BUS Diff. CTs and FDR CTs (unit 6 &12)
7 | SEL | 751201A1A1A70851680 | SEL 751 feeder protection relay | 15 | Feeder protection relay
8 | SEL | 0735BX00944CXXXXXX16101XX | SEL 735 Power Quality and Revenue Meter | 2 | Metering relay
9 | GE | 850EP1NNG1HNNAANAAPCA4FCNB4043X HID-3-0 | GE 850 High-Impedance Differential Relay and High-Impedance DIFFRENTIAL Module | 2 | High impedance bus differential
10 | ABB | C129A501G01 | FT-1 test switch, 10 pole, P1 P1 P1 P1 P1 P1 P1 P1 P1 P1 | 19 | PT reference to relay, 2 BUS diff 86 trip
11 | ABB | C498A020G01 | FT-1 test switch, 10 pole, C1-C1 C1-C1 C1-C1 C1-C1 C1-C1 | 19 | CT reference to relay
12 | Shallco | 2638D | Control switch, 125vdc | 30 | Breaker operation
13 | Shallco | 7603D | 86 lockout relay, 125vdc | 15 | Breaker operation
14 | Shallco | 7610D | 86 lockout relay, 125vdc | 2 | High impedance Bus protection breaker operation
15 |  |  | Red lights | 30 | Breaker closed
16 |  |  | Green lights | 30 | Breaker open
17 |  |  | White lights | 34 | 86 Healthy
18 |  |  | 6A triple fuse holder (HOLDER) | 20 | PT secondary fuses each unit
19 |  |  | 6A four fuse holder (HOLDER) | 2 | PT secondary fuses on BUS PT units
20 |  |  | 6A fuses, AC- rated (FUSE) | 68 | PT secondary fuses, AC
21 |  |  | 30A Double fuse, DC- rated with fuse holder | 30 fuses, 15 holders | trip circuit DC
22 |  |  | 3A Double fuse, DC- rated with fuse holder | 38 fuses, 19 holders | relay power circuit DC
23 |  |  | 15A Double fuse, DC- rated with fuse holder | 32 fuses, 16 holders | close circuit DC, etheret switch ckt.
24 | ABB | A2A200TT | 225A 208Y/120V Lighting Panel | 1 | Lighting Panel
25 | ABB | XT5NU360BBYN000XXX | 600A 480Y/277V Power Panel | 1 | 480V Power Panel
26 | Hamond | SG3A0075KB | 75kVA XFMR 480V-208Y/120V 60Hz | 1 | Lighting Panel XFMR
27 | ABB | TH3361R | Fusible Switch 30A 3P HD N3R 600V | 2
28 | Siemens | 5SJ4225-7HG41 | SENTRON / 5SJ4 miniature circuit breaker, 25 A, 2-pole, C-curve, UL 489 / CSA, 240 Vac max under UL, 14 kA interrupting rating, DIN-rail mount | 1 | Heater/ humidity sensor
29 | Siemens | CQD215 | 2-pole, 15 A, UL 489 MCCB, 125/250 VDC | 19 | Local unit 125 VDC MCB between Mersen PDB and local DC1/DC2 terminal blocks
30 | Siemens | CQD260 | 2-pole, 60 A, UL 489 MCCB, 125/250 VDC | 1 | Main 125 VDC switchgear distribution MCB upstream of DCP/DCN trunk
31 | Mersen | MPDB66511 | 1P Copper Power Distribution Block, 1000VAC/DC,350A | 38 | Two 1-pole blocks per unit for 125vdc distribution
32 | GEIS | LL10-W | Lamp 220V | 19
32 | GEIS | A6M2C04 | Heater MCB No.81056AEN | 19
32 | GEIS | LXW20-11- | Position switch | 19
32 | GEIS | LWK-Z3T8(TH) | 220VAC Temp& humidity monitor | 19
32 | GEIS | SB-G | 100W 220VAC heater | 38
32 | GEIS | DXN8B- 7.2 | Potential indicator 40.5kV-60Hz/Q2(AC/DC 125V)-TH- BROWN, ORANGE, YELLOW- L1 L2 L3 | 19