## 8478
Item No. | Manufacturer | Part Number | Description | Quantity | Application | Action
1 | GEIS | VB-40.5/T1250-31.5W | Withdrawable VCB, 38kV, 1250A, 31.5kA | 1
2 |  |  | Potential transformer, 34.5kV/120V, 500VA, 1 per phase | 3 | Breaker line side | PTs need to be replaced Y-Y
3 |  |  | Current transformer, 1000:5A, 1 per phase | 3 | Breaker line side | Current CTs need to be repalced :5A
4 |  |  | Fused CPT, 34.5kV/120V, 2500VA | 1 | Control power primary source
5 | SEL |  | SEL 751 feeder protection relay | 1 | Protective relay
6 |  |  | 2A E-Rated fuse | 2 | CPT Primary
7 | Weidmuller | BR2C30UC | 30A, 2P circuit breaker, 120VAC | 1 | CPT secondary | https://www.mouser.com/ProductDetail/Weidmuller/2478220000?qs=QNEnbhJQKvbTm%2F2QHjRY6Q%3D%3D&srsltid=AfmBOop4b5gsEnFSkeER6Pgk7__9C7mdJdDcuqzoBwdud0zTjUFPt6vV
8 | Weidmuller | BR1C30UC | 30A, 1P circuit breaker, 120VAC | 1 | Shore power | https://www.mouser.com/ProductDetail/Weidmuller/2477970000?qs=QNEnbhJQKvYZ3ReBGy3dbA%3D%3D&srsltid=AfmBOoo1W7ANhh74Ci3BX74r-17wFNADO23jtNcSZ3T5-2a3uIUI6bCw
9 | Bluesea | 9010 | AC Rotary Switch - OFF + 3 Positions 120V AC 30A | 1 | Source selector switch
10 | Leviton | 99W47-S | 30 Amp, 125 Volt, NEMA L5-30, 2P, 3W, Locking Single Outlet, Industrial Grade, Grounding, Wetguard - YELLOW | 1 | Shore power receptacle
11 | Eaton | SMART3000RM2U | Tripp Lite series SmartPro 3000VA 3000W 120V Line | 1 | Control power primary source
12 | Heatrex | 276-19 | Space heaters, HEATREX tubular space heater, Type 1 Rated 500W @ 240VAC,including steel shroud and mounting bracket, UL/CSA recognized. Operate 125W @ 120VAC | 3 | Space heaters
13 | Finder | 7T.81.0.000.2403 | Thermostat, panel thermostat, 1 NC contact, adjustable 0 to 60°C, DIN-rail mount, for heater control | 1 | Thermostat
14 | Weidmuller | BR1C15UC | 15A, 1P circuit breaker, 120VAC | 1 | heater circiut breaker | https://www.mouser.com/ProductDetail/Weidmuller/BR1C15UC?qs=pUKx8fyJudD9a%252BuK093ZeQ%3D%3D&srsltid=AfmBOoqc9iP9pj87nHTj3ykh4zg286s1tMNMwEKubJFV5noppzJ22u03
15 |  |  | Triple fuse holder with 6A fuses | 3 | PT secondary | OTM6 mersen midget fuse, 6a
16 | ABB | C129A501G01 | FT-1 test switch, 10 pole, P1 P1 P1 P1 P1 P1 P1 P1 P1 P1 | 1 | PT
17 | ABB | C498A020G01 | FT-1 test switch, 10 pole, C1-C1 C1-C1 C1-C1 C1-C1 C1-C1 | 1 | CT
18 | Absopulse | PFH65F-A/125F3WT-U8809 | 1000W, Industrial Quality Power Supply 120Vac to 125Vdc/8A | 1 | Control power primary source
19 | Weidmuller | BR2C30UC | 30A, 2P circuit breaker, 125VDC | 1 | Power supply output | https://www.mouser.com/ProductDetail/Weidmuller/2478220000?qs=QNEnbhJQKvbTm%2F2QHjRY6Q%3D%3D&srsltid=AfmBOop4b5gsEnFSkeER6Pgk7__9C7mdJdDcuqzoBwdud0zTjUFPt6vV
20 |  |  | Double fuse holder with 30A fuses-125VDC | 1 | Close circuit | ATM30 mersen midget fuse, 30a
21 | Shallco | 2638D125VDCX | Control switch, 125vdc | 1 | breaker operation
22 | Shallco | 7603D125VDCX | 86 lockout relay, 125vdc | 1 | breaker operation
23 | C3CONTROLS | MRL125DLR-MPLLRD | SERIES F, 16MM, 125VDC AC/DC REISTOR LIGHT LED RED WITH RED LENS | 1 | breaker indication
24 | C3CONTROLS | MRL125DLW‑MPLLWE | SERIES F, 16MM, 125VDC AC/DC REISTOR LIGHT LED GREEN WITH White LENS | 1 | breaker indication
25 | C3CONTROLS | MRL125DLG-MPLLGN | SERIES F, 16MM, 125VDC AC/DC REISTOR LIGHT LED GREEN WITH GREEN LENS | 1 | breaker indication
26 |  |  | Pendant control (BRCT)- Red/Green light/push button 30MM C3 ¦ ZPEKL-1012-317PN Male Plug ¦ ZREP-12-317SN Female Receptacle ¦ 10C16AWG 15’ cable ¦ HBL 073031203A Hubble Strain Relief | 1 | remote BRCT
27 |  |  | Capacitor trip device | 2 | For breaker trip and 86 trip | needs evaluation
28 |  |  | Double fuse holder with 30A fuses-125DC | 1 | Trip circuit | ATM30 mersen midget fuse, 30a
29 |  |  | Double fuse holder with 15A fuses-125DC | 1 | SEL 751 ckt | ATM15 mersen midget fuse, 15a
30 |  |  | TB1-4 (terminal block, 4pos) | 1 | PT reference
31 |  |  | TB2-8 (terminal block, 8pos) | 1 | CPT/ control power ckt
32 |  |  | TB3-8 (terminal block, 8pos) | 1 | control sch
33 |  |  | SB1-4(shorting terminal block, 4pos) | 1 | CT reference