## Project
Project intake - supplied once per job
Fill the Value column. Yellow rows are required before drafting starts.
Field | Value | What it is
job | FIXTURE-TWOHIGH | IOM job number, e.g. 8372
customer |  | End customer name
title | Two-high regression fixture | Project title as it appears in the title block
location_code |  | e.g. +A01
sheet_standard |  | Which drawing standard / frame profile to use
system_voltage | 13.8kV | Nominal system voltage, e.g. 4.16kV
bus_rating | 1200A | Continuous bus rating, e.g. 4000A
bus_ka_rating | 25kA | Bus short-circuit rating, e.g. 50kA
phases | 3 | e.g. 3
wires |  | e.g. 3W
frequency | 60HZ | e.g. 60HZ
available_sc_current |  | Available short-circuit current AT the switchgear (Incoming Power spec)
bil |  | Basic insulation level, if shown on the bus label
grounding |  | System grounding arrangement
drawing_no |  | e.g. 8372+A01-001
rev
date
engineer
drawn
checked
approved

## Units
unit | bus | deck | tag | description | voltage | amp_rating | ka_rating | relay | ct_protection | ct_differential | ct_metering | ct_ground | pt | pt_primary_fuse | destination
1 | A | lower | 52-M | MAIN BREAKER | 15kV | 1200A | 25kA | SEL-751 | 1200:5A (3) | [5 empty] | UTILITY SUPPLY 13.8kV, 3PH, 60HZ
1 | A | upper |  | BUS PT | [8 empty] | 14,400:120V | CLF 0.5E
2 | A | lower | 52-F1 | TRANSFORMER FEEDER | 15kV | 600A | 25kA | SEL-751 | 200:5A (3) | [5 empty] | TO 2500kVA XFMR 13.8kV-480Y/277V
2 | A | upper | 52-F2 | MOTOR FEEDER | 15kV | 600A | 25kA | SEL-710 | 100:5A (3) |  |  | 50:5A |  |  | TO 1500HP 13.8kV MOTOR
3 | A | single | 52-F3 | FUTURE FEEDER | 15kV | 600A | 25kA | SEL-751 | 400:5A (3) | 400:5A (3) |  |  |  |  | RESERVED FOR FUTURE REQUIREMENT

## Field guide
What each column on the Units tab means
Column | Meaning
unit | Cubicle number. Two rows share it on a two-high cubicle.
bus | Which bus the cubicle sits on.
deck | single, or upper / lower for the two decks of a two-high cubicle.
tag | Device tag, e.g. 52-GEN1A. Unique within the lineup.
description | Cubicle title printed under the unit number.
voltage | Breaker rated maximum voltage, e.g. 15kV.
amp_rating | Breaker continuous current. BLANK MEANS NO BREAKER -- that is how a deck holds only a bus PT.
ka_rating | Breaker interrupting rating.
relay | Protection relay model. Drawn as a labelled box beside the breaker.
ct_protection | Protection CT ratio and quantity, e.g. 400:5A (3).
ct_metering | Metering CT. Fill this ONLY if the cubicle really has a second CT set -- leaving it blank is what keeps one-CT feeders to one CT.
ct_ground | Separate ground-fault CT, e.g. 50:5A. Motor feeders.
pt | Bus PT ratio, e.g. 14,400:120V. The cubicle that states this gets the PT branch, and its secondary feeds every relay in the lineup.
pt_primary_fuse | PT primary fuse, e.g. CLF 0.5E. The secondary fuse belongs on the three-line diagram, not here.
destination | Source or load text printed at the cubicle entry / exit. A future feeder is a normal feeder whose destination says so.
A device is drawn if and only if its cell has a value.